## Sheet1
Interior Lighting and Exit Signs Power Calculation
Section 1:Energy Analysis - Tabular
Code chapter and/or standard used for design. NYC ECC 2020 - Chapter C4
Project Occupancy: |  |  | BBO - ROOSEVELT (360 PULASKI AVE.)
Alteration - Lighting Fixture Installation
Climate zone: |  | 4A
NYCECC Citation |  | Provision |  |  | Item Description |  |  | Proposed Design Value |  |  |  | Code Prescriptive Value |  | Supporting Documentation (Drawings)
C405.2.1.1 |  | Interior lighting controls |  |  | Interior lighting controls include manual, vacancy, and occupant sensor controls. |  |  | Interior lighting controls have been provided in accordance with C405.2.1.1and C405.2.2.2 |  |  |  | Lighting systems shall be provided with controls as required in Sections C405.2.1.1and C405.2.2.2 |  | See drawings: T001.00, E001.00, E101.00, E703.00
C405.2.2.3 |  | Daylight zone control |  |  | Day light zone control for spaces with vertical fenestration |  |  | Manual Daylight Controls has been provided in accordance with C405.2.2.3.1 |  |  |  | Day light zone control as per C405.2.2.3.1 Manual Daylight Control |  | See drawings: T001.00, E001.00, E101.00, E703.00
C405.4 |  | Exit Signs |  |  | Exit Sign Replacement |  |  | Watts per side of Internally illuminated exit signs are less than 5 watts in accordance with C405.4 |  |  |  | Internally illuminated exit signs shall not exceed 5 watts per side as per C405.4 |  | See drawings: T001.00, E001.00, E101.00, E703.00,
BBO - ROOSEVELT (360 PULASKI AVE.)
C405.5.2 |  | Interior lighting power |  |  | Lighting Power Density of School building: |  |  | Lighting Power Density (LPD): |  |  | 0.896 Watts/ft² | The total interior lighting power (Watts) is the sum of interior lighting for all areas of the building covered in this permit. Lighting Power Density (LPD) allowance: 1.2Watts/ft² |  | See drawings: T001.00, E001.00, E101.00, E703.00
BBO - ROOSEVELT (360 PULASKI AVE.)
[8 empty] | PASSES |  | 0.8957 | Watts/ft² | < | 1.2 Watts/ft²
[10 empty] | 0 | Watts | < | 5 Watts/Side
Section 2: Interior Lighting and Power Calculation
Building | A | [6 empty] | B | C | D | E | F |  | G
| Fixture ID: Description / Lamp / Wattage Per Lamp / Ballast |  |  |  |  | Lamp Watts | Ballast Factor | Lamps/ Fixture | #of Fixtures | Fixture Watt. | (C X D) Total Watt. | AREA |  | (E/F ) LPD (Watts/Sq.ft)
BBO - ROOSEVELT (360 PULASKI AVE.) | L1 | LOUIS POULSEN, LP CIRCLE 10.5"- SURFACE MOUNT |  |  |  | 30 | 0.88 | 1 | 54 | 26 | 1404 | 5310 |  | 0.89567
| L2 | LOUIS POULSEN, LP CIRCLE 18.0"- SURFACE MOUNT |  |  |  | 25 | 0.88 | 1 | 28 | 22 | 616
| L3 | LOUIS POULSEN, LP ROUND 17.2"- SUSPENDED |  |  |  | 54 | 0.88 | 2 | 5 | 95 | 475
| L4 | LOUIS POULSEN, LP ROUND 26.7"- SUSPENDED |  |  |  | 54 | 0.88 | 4 | 6 | 190 | 1140
| L5 | LITHONIA STL2 SURFACE/SUSPENDED |  |  |  | 39 | 0.88 | 2 | 6 | 69 | 414
| L6 | LITHONIA STL4 SURFACE/SUSPENDED |  |  |  | 45.2 | 0.88 | 4 | 3 | 159 | 477
| L7 | GARDCO SOFTVIEW SVPG-266L-1200-WW-G2-X/SURFACE MOUNT |  |  |  | 52 | 0.88 | 1 | 5 | 46 | 230
| CF | REPLACE LAMP WITH COMPACT FLUORESCENT |  |  |  | 32 | 1 | 1 | 0 | 32 | 0
| C | 1'X4' SURFACE MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| C1 | 1'X8' SURFACE MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 4 | 0 | 113 | 0
| D | 1'X4' SURFACE MOUNTED WRAPAROUND FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| D1 | 1'X4' PENDANT MOUNTED WRAPAROUND FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| E | 1'X4' PENDANT MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| F1 | 8' LONG OPEN REFLECTOR INDUSTRIAL FIXTURE |  |  |  | 32 | 0.88 | 4 | 0 | 113 | 0
| G | 1'X4' SURFACE MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| G2 | 1'X8' SURFACE MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| H | 1'X4' PENDANT MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| H1 | 1'X8' PENDANT MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| M1 | 1'X4' RECESSED MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| M2 | 1'X8' RECESSED MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 4 | 0 | 113 | 0
| M17 | 1'X8' RECESSED MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| M18 | 1'X4' RECESSED MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 1 | 0 | 28 | 0
| S11 | 1/2'X2' SURFACE MOUNTED FIXTURE |  |  |  | 17 | 0.88 | 2 | 0 | 30 | 0
| N2 | 2'X4' RECESSED MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| O1 | 4' HAZARDOUS LOCATION LTG. FIXT, 20 GAUGE CRC HOUSING WITH ACRYLIC LENS COMPLETELY SEALED AND GASKETED. CONFIRM MOUNTING TYPE BEFORE ORDERING |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| S1 | 1/2'X2' SURFACE MOUNTED FIXTURE |  |  |  | 17 | 0.88 | 2 | 0 | 30 | 0
| S2 | 1/2'X4' SURFACE MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| S11 | 1/2'X2' SURFACE MOUNTED FIXTURE |  |  |  | 17 | 0.88 | 2 | 0 | 30 | 0
| U1 | 12" ROUND COMPACT FLUORESCENT FIXTURE |  |  |  | 42 | 1 | 1 | 0 | 42 | 0
| W1 | 1'X4' SURFACE MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| W2 | 1'X4' RECESSED MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| W5 | 1'X8' RECESSED MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 4 | 0 | 113 | 0
| Y | SURFACE MOUNT LED HIGHBAY FIXTURE WITH TEXTURED ACRYLIC LENS |  |  |  | 55.4 | 1 | 1 | 0 | 55 | 0
| Y1 | LED HIGHBAY FIXTURE WITH TEXTURED ACRYLIC LENS AND STEM PENDANT |  |  |  | 85 | 1 | 1 | 0 | 85 | 0
| F | 4' LONG OPEN REFLECTOR INDUSTRIAL FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| F1 | 8' LONG OPEN REFLECTOR INDUSTRIAL FIXTURE |  |  |  | 32 | 0.88 | 4 | 0 | 113 | 0
| M15 | 1'X8' RECESSED MOUNTED FIXTURE |  |  |  | 32 | 1.15 | 2 | 0 | 74 | 0
| M16 | 1'X4' RECESSED MOUNTED FIXTURE |  |  |  | 32 | 1.15 | 1 | 0 | 37 | 0
| M8 | 1/2'X4' RECESSED MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| M3 | 1'X4' SURFACE MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| M4 | 1'X8' SURFACE MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 4 | 0 | 113 | 0
| V1 | DISPLAY LIGHT 1'X4' WITH 1-T8 L |  |  |  | 32 | 0.88 | 1 | 0 | 28 | 0
| T | 8" RECESSED DOWNLIGHT, LED, WITH DECORATIVE WHITE TRIM RING |  |  |  | 27.6 | 1 | 1 | 0 | 28 | 0
| T4 | PENDANT MOUNTED SINGLE LED WITH 12" REFRACTORS AND CONICAL LENS |  |  |  | 32 | 1 | 1 | 0 | 32 | 0
| A7 | 1'X8' PENDANT MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| A8 | 1'X4' PENDANT MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 1 | 0 | 28 | 0
| DA | 1'X4' SURFACE MOUNTED WRAPAROUND FIXTURE |  |  |  | 32 | 0.88 | 1 | 0 | 28 | 0
| D1A | 1'X4' PENDANT MOUNTED WRAPAROUND FIXTURE |  |  |  | 32 | 0.88 | 1 | 0 | 28 | 0
| B7 | 1'X8' SURFACE MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 2 | 0 | 56 | 0
| B8 | 1'X8' SURFACE MOUNTED FIXTURE |  |  |  | 32 | 0.88 | 1 | 0 | 28 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total watts | 4756
Section 3: Exit Signage Power Calculation
School Building | A | [6 empty] | B | C | D | E | F
| Exit Sign Fixture ID: Description |  |  |  |  | Lamp Watts | Ballast Factor | Lamps/ Fixture | #of Fixtures | Fixture Watt. | Faces per Fixture | (C X D) Total Watts. |  | Watts per side of Exit sign Fixture =D/E
BBO - ROOSEVELT (360 PULASKI AVE.) | X1 | MULE LIGHTING NYELX |  |  |  | 5 | 1 | 1 | 12 | 5 | 1 | 60 |  | 5
| X2 | EDGE MOUNT-DOUBLE FACE- LED EXIT SIGNAGE |  |  |  | 3.5 | 1 | 1 | 0 | 3.5 | 2 | 0
| X3 | PENDANT MOUNT-SINGLE FACE-LED EXIT SIGNAGE |  |  |  | 3.5 | 1 | 1 | 0 | 3.5 | 1 | 0
| X4 | PENDANT MOUNT-DOUBLE FACE-LED EXIT SIGNAGE |  |  |  | 3.5 | 1 | 1 | 0 | 3.5 | 2 | 0
| X5 | WALL SURFACE MOUNT-SINGLE FACE-LED EXIT SIGNAGE |  |  |  | 3.5 | 1 | 1 | 0 | 3.5 | 1 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Section 3:Compliance Statement:
Compliance Statement: The proposed lighting design represented in this document is consistent with the building plans, specifications and other calculations submitted with this permit application. The proposed lighting system has been designed to meet the 2014 New York City Energy Conservation Code requirement and comply with mandatory requirements in the Requirements Checklist.
XXX | [9 empty] | XXX
Name - Title |  |  |  | Signature | [5 empty] | Date

## Sheet2 (hidden)
FIXT. TYPE | MANUFACTURER'S DESCRIPTION | MANUFACTURER'S CATALOG# | LAMPS |  | VOLTS | BALLAST FACTOR | MOUNTING | TYPICAL LOCATION |  |  |  | BALLAST FACTOR | LAMPS | watts
Block:1X8 Pendant mount | 1'X8' PENDANT MOUNTED FIXTURE SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. LENS TO BE 25% DR ACRYLIC. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" AND SLIDING STEM ADJUSTMENT PLATES. | LSI #88-8-232-SSOHLR1.15-UE-DR-SCA MERCURY #M110-132OCT/8T-A125-25%DR-WORT-ELBSH-UNI-P1 LEGION #4312-132-8T-ACP-PT-SACH-RLA NATIONAL #PSPKLA-132-8'-UNV-RSB-1.15BF CORONET #BCF-8-132T8-UNV-1.15-25%DR-PS RENOVA #MPW8-M-N-232-UNV-12H-RST-QP1-NYC-TL-AP LUMAX #WB23296-EO9IA-EAR-PSPH-MNL2-2G-SCA1 | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | 1.15 MIN. PROGRAM RAPID START | PENDANT | CLASSROOM/ OFFICES | 73.6 | A1 | 1'X8' PENDANT MOUNTED FIXTURE | 1.15 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' PENDANT MOUNTED FIXTURE SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. LENS TO BE 25% DR ACRYLIC. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" AND SLIDING STEM ADJUSTMENT PLATES. | LSI #88-4-132-SSOHLR1.15-UE-DR-SCA MERCURY #M110-132OCT-A125-25%DR-WORT-ELBSH-UNI-P1 LEGION #4312-132-ACP-PT-SACH-RLA NATIONAL #PSPKLA-132-4'-UNV-RSB-1.15BF CORONET #BCF-4-132T8-UNV-1.15-25%DR-PS RENOVA #MPW4-M-N-132-UNV-1H-RST-QP1-NYC-TL-AP LUMAX #WB13248-EO9IA-EAR-PSPH-MNL2-2G-SCA1 | 1 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | 1.15 MIN. PROGRAM RAPID START | PENDANT | CLASSROOM/ OFFICES | 36.8 | A2 | 1'X4' PENDANT MOUNTED FIXTURE | 1.15 | 1 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' PENDANT MOUNTED FIXTURE SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. LENS TO BE 25% DR ACRYLIC. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" AND SLIDING STEM ADJUSTMENT PLATES. | LSI #88-8-432-SSOHLR1.15-UE-DR-SCA MERCURY #M110-232OCT/8T-A125-25%DR-WORT-ELBSH-UNI-P1 LEGION #4312-232-8T-PT-SACH-RLA NATIONAL #PSPKLA-232-8'-UNV-RSB-1.15BF CORONET #BCF-8-232T8-UNV-1.15-25%DR-PS RENOVA #MPW8-M-N-432-UNV-14H-RST-QP1-NYC-TL-AP LUMAX #WB43296-CO9IA-EAR-PSPH-MNL2-2G-SCA1 | 4 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | 1.15 MIN. PROGRAM RAPID START | PENDANT | CLASSROOM/ OFFICES | 147.2 | A3 | 1'X8' PENDANT MOUNTED FIXTURE | 1.15 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' PENDANT MOUNTED FIXTURE SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. LENS TO BE 25% DR ACRYLIC. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" AND SLIDING STEM ADJUSTMENT PLATES. | LSI #88-4-232-SSOHLR1.15-UE-DR-SCA MERCURY #M110-232OCT-A125-25%DR-WORT-ELBSH-UNI-P1 LEGION #4312-232-ACP-PT-SACH-RLA NATIONAL #PSPKLA-232-4'-UNV-RSB-1.15BF CORONET #BCF-4-232T8-UNV-1.15-25%DR-PS RENOVA #MPW4-M-N-232-UNV-12H-RST-QP1-NYC-TL-AP LUMAX #WB23248-EO9IA-EAR-PSPH-MNL2-2G-SCA1 | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | 1.15 MIN. PROGRAM RAPID START | PENDANT | CLASSROOM/ OFFICES | 73.6 | A4 | 1'X4' PENDANT MOUNTED FIXTURE | 1.15 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X3 TYPE FIXTURE | 1'X3' PENDANT MOUNTED FIXTURE SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. LENS TO BE 25% DR ACRYLIC. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" AND SLIDING STEM ADJUSTMENT PLATES. | LSI #88-3-125-SSOHLR1.15-UE-DR-SCA MERCURY #M110-125OCT-A125-25%DR-WORT-ELBSH-UNI-P1 LEGION #4312-125-ACP-PT-SACH-RLA NATIONAL #PSPKLA-125-3'-UNV-RSB-1.15BF CORONET #BCF-3-125-UNC-1.15-25%DR-PS RENOVA #MPW3-M-N-125-UNV-1H-RST-QP1-NYC-TL-AP LUMAX #WB12503-EO9IA-EAR-PSPH-MNL2-2G-SCA1 | 1 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | 1.15 MIN. PROGRAM RAPID START | PENDANT | CLASSROOM/ OFFICES | 36.8 | A5 | 1'X3' PENDANT MOUNTED FIXTURE | 1.15 | 1 | 25 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' PENDANT MOUNTED FIXTURE SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. LENS TO BE 25% DR ACRYLIC. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" AND SLIDING STEM ADJUSTMENT PLATES. | LSI #88-4-332-SSOHLR1.15-UE-DR-SCA MERCURY #M110-332OCT-A125-25%DR-WORT-ELBSH-UNI-P1 LEGION #4312-332-ACP-PT-SACH-RLA NATIONAL #PSPKLA-332-4'-UNV-RSB-1.15BF CORONET #BCF-4-332T8-UNV-1.15-25%DR-PS RENOVA #MPW4-M-N-332-UNV-1H-RST-QP1-NYC-TL-AP LUMAX #WB33248-CO9IA-EAR-PSPH-MNL2-2G-SCA1 | 3 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | 1.15 MIN. PROGRAM RAPID START | PENDANT | CLASSROOM/ OFFICES | 110.4 | A6 | 1'X4' PENDANT MOUNTED FIXTURE | 1.15 | 3 | 25 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' SURFACE MOUNTED FIXTURE WITH CLEAR 25% DR ACRYLIC LENS, SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" | LSI #88-8-232-SSOHLR1.15-UE-DR-SCA MERCURY #M110W-132OCT/8T-A125-25%DR-WORT-ELBSH-UNI-P1 LEGION #4312-132-8T-ACP-PT-SACH-RLA NATIONAL #PSPKLA-132-8'-UNV-RSB-1.15BF CORONET #BCF-8-132-UNV-1.15-100%DR RENOVA# MPWS8-M-N-232-UNV-12H-RST-QP1-NYC-TL LUMAX #WB23296-EO9IA-EAR-PSPH-MNL2-2G-SCA1 | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | 1.15 MIN. PROGRAM RAPID START | SURFACE | CLASSROOM/ OFFICES | 73.6 | B1 | 1'X8' SURFACE MOUNTED FIXTURE | 1.15 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' SURFACE MOUNTED FIXTURE WITH CLEAR 25% DR ACRYLIC LENS, SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" | LSI #88-4-132-SSOHLR1.15-UE-DR-SCA MERCURY #M110W-132OCT-A125-25%DR-WORT-ELBSH-UNI-P1 LEGION #4312-132-ACP-PT-SACH-RLA NATIONAL #PSPKLA-132-4'-UNV-RSB-1.15BF CORONET #BCF-4-132T8-UNV-1.15-100%DR RENOVA #MPWS4-M-N-132-UNV-1H-RST-QP1-NYC-TL LUMAX #WB13248-EO9IA-EAR-PSPH-MNL2-2G-SCA1 | 1 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | 1.15 MIN. PROGRAM RAPID START | SURFACE | CLASSROOM/ OFFICES | 36.8 | B2 | 1'X4' SURFACE MOUNTED FIXTURE | 1.15 | 1 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' SURFACE MOUNTED FIXTURE WITH CLEAR 25% DR ACRYLIC LENS, SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" | LSI #88-8-432-SSOHLR1.15-UE-DR-SCA MERCURY #M110W-232OCT/8T-A125-25%DR-WORT-ELBSH-UNI P1 LEGION #4312-232-8T-ACP-PT-SACH-RLA NATIONAL #PSPKLA-232-8'-UNV-RSB-1.15BF CORONET #BCF-8-232T8-UNV-1.15-100%DR RENOVA #MPWS8-M-N-432-UNV-14H-RST-QP1-NYC-TL LUMAX #WB43296-CO9IA-EAR-PSPH-MNL2-2G-SCA1 | 4 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | 1.15 MIN. PROGRAM RAPID START | SURFACE | CLASSROOM/ OFFICES | 147.2 | B3 | 1'X8' SURFACE MOUNTED FIXTURE | 1.15 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' SURFACE MOUNTED FIXTURE WITH CLEAR 25% DR ACRYLIC LENS, SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" | LSI #88-4-232-SSOHLR1.15-UE-DR-SCA MERCURY #M110W-232OCT-A125-25%DR-WORT-ELBSH-UNI P1 LEGION #4312-232-ACP-PT-SACH-RLA NATIONAL #PSPKLA-232-4'-UNV-RSB-1.15BF CORONET #BCF-4-232T8-UNV-1.15-100%DR RENOVA #MPWS4-M-N-232-UNV-12H-RST-QP1-NYC-TL LUMAX #WB23248-EO9IA-EAR-PSPH-MNL2-2G-SCA1 | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | 1.15 MIN. PROGRAM RAPID START | SURFACE | CLASSROOM/ OFFICES | 73.6 | B4 | 1'X4' SURFACE MOUNTED FIXTURE | 1.15 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X3 TYPE FIXTURE | 1'X3' SURFACE MOUNTED FIXTURE SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. LENS TO BE 25% DR ACRYLIC. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" | LSI #88-3-125-SSOHLR1.15-UE-DR-SCA MERCURY #M110W-125OCT-A125-25%DR-WORT-ELBSH-UNI P1 LEGION #4312-125-ACP-PT-SACH-RLA NATIONAL #PSPKLA-125-3'-UNV-RSB-1.15BF CORONET #BCF-3-125T8-UNV-1.15-25%DR RENOVA #MPWS3-M-N-125-UNV-1H-RST-QP1-NYC-TL LUMAX #WB12503-EO9IA-EAR-PSPH-MNL2-2G-SCA1 | 1 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | 1.15 MIN. PROGRAM RAPID START | SURFACE | CLASSROOM/ OFFICES | 36.8 | B4 | 1'X3' SURFACE MOUNTED FIXTURE | 1.15 | 1 | 32 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' SURFACE MOUNTED FIXTURE WITH CLEAR 25% DR ACRYLIC LENS. | KENALL #MLHA12-48-R-MW-CP-232-IS-1-DV LSI #88-4-232-SSO10-UE-DR-SCA MERCURY #M110W-232OCT-A125-25%DR-WORT-ELB LEGION #4312-232-ACP-PT-SACH-LBF-RLA NATIONAL #PSPKLA-232-4'-UNV-RSB-.88BF CORONET #BCF-4-232T8-UNV-100%DR RENOVA #MPWS4-M-N-232-UNV-12N-NYC-TL LUMAX #WB23248-EO9IA-EAR-PSPH-MNL2-2G-SCA1 | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 PROGRAM RAPID START | SURFACE | OFFICES, CORRIDORS, TOILETS, UTILITY/STORAGE ROOMS | 56.32 | C | 1'X4' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' SURFACE MOUNTED FIXTURE WITH CLEAR 25% DR ACRYLIC LENS. | KENALL #MLHA12-96-R-MW-CP-232-IS-1-DV LSI #88-8-432-SSO10-UE-DR-SCA MERCURY #M110W-232OCT/8T-A125-25%DE-WORT-ELB LEGION #4312-232-8T-ACP-PT-SACH-LBF-RLA NATIONAL #PSPKLA-232-8'-UNV-RSB-.88BF CORONET #BCF-8-232T8-UNV-100%DR RENOVA #MPWS8-M-N-432-UNV-14N-NYC-TL LUMAX #WB43296-CO9IA-EAR-PSPH-MNL2-2G-SCA1 | 4 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 PROGRAM RAPID START | SURFACE | OFFICES, CORRIDORS, TOILETS, UTILITY/STORAGE ROOMS | 112.64 | C1 | 1'X8' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:14 inch ROUND FIXTURE | REPLACE LAMP WITH COMPACT FLUORESCENT |  | 1 | 32W- COMPACT FLUORESCENT 4K COLOR TEMP | 120 |  |  | STAIRWAYS/ CORRIDORS, TOILETS, UTILITY/STORAGE ROOMS |  | CF | REPLACE LAMP WITH COMPACT FLUORESCENT | 1 | 1 | 32 | 32W- COMPACT FLUORESCENT 4K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' SURFACE MOUNTED WRAPAROUND FIXTURE WITH PRISMATIC POLYCARBONATE HIGH IMPACT LENS | KENALL #SH1248-232-IS-1-DV MERCURY #M50VPW-132OCT-ELB-UNI NATIONAL #BFPLEX-14-232-SM-T8-VOLT-EB-4' LSI #471-S-2-32-SSOHLR-TORX-K19-UE NEWSTAR #51HD4-2-32-1-B-UN CORONET #SVP-4-232T8-BP-UNV LUMAX #VR23248-EO9-P-D12W | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | STAIRWAYS/ CORRIDORS, |  | D | 1'X4' SURFACE MOUNTED WRAPAROUND FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' PENDANT MOUNTED WRAPAROUND FIXTURE WITH PRISMATIC POLYCARBONATE HIGH IMPACT LENS | KENALL #SH1248-232-IS-1-DV MERCURY #M50VPW-132OCT-ELB-UNI NATIONAL #BFPLEX-14-232-PM-T8-VOLT-EB-4' LSI #471-S-2-32-SSOHLR-TORX-K19-UE-TANDEM NEWSTAR #51HD4-2-32-1-B-UN-TANDEM CORONET #SVP-4-232T8-BP-UNV-PS LUMAX #VR23248-EO9-P-D12W-2S | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | PENDANT | STAIRWAYS/ CORRIDORS, |  | D1 | 1'X4' PENDANT MOUNTED WRAPAROUND FIXTURE | 0.88 | 2 | 25 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' PENDANT MOUNTED FIXTURE SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. LENS TO BE 25% DR ACRYLIC. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" | KENALL #R548-232-IS-1-DV LSI #88-4-232-SSO10-UE-DR-SCA MERCURY #M110-232OCT-A125-25%DR-WORT-ELB-UNI-P1 LEGION #4312-232-ACP-PT-SACH-LBF-RLA NATIONAL #PSPKLA-232-4'-UNV-RSB-.88BF CORONET #BCF-4-232T8-UNV-100%DR-PS RENOVA #MPW4-M-N-232-UNV-1N-NYC-TL LUMAX #WB23248-EO9IA-EAR-PSPH-MNL2-2G-SCA1 | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 PROGRAM RAPID STAR | PENDANT | CORRIDORS, TOILETS, UTILITY/STORAGE ROOMS |  | E | 1'X4' PENDANT MOUNTED FIXTURE | 0.88 | 2 | 25 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' PENDANT MOUNTED FIXTURE SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. LENS TO BE 25% DR ACRYLIC. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" | KENALL #R548-132-IS-1-DV LSI #88-4-132-SSO10-UE-DR-SCA MERCURY #M110-132OCT-A125-25%DR-WORT-ELB-UNI-P1 LEGION #4312-232-ACP-PT-SACH-LBF-RLA NATIONAL #PSPKLA-132-4'-UNV-RSB-.88BF CORONET #BCF-4-132T8-UNV-PS RENOVA #MPW4-M-N-132-UNV-1N-NYC-TL LUMAX #WB13248-EO9IA-EAR-PSPH-MNL2-2G-SCA1 | 1 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 PROGRAM RAPID STAR | PENDANT | CORRIDORS, TOILETS, UTILITY/STORAGE ROOMS |  | E1 | 1'X4' PENDANT MOUNTED FIXTURE | 0.88 | 1 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' PENDANT MOUNTED FIXTURE SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. LENS TO BE 25% DR ACRYLIC. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" | KENALL #R596-232-IS-1-DV LSI #88-8-432-SSO10-UE-DR-SCA MERCURY #M110-232OCT/8T-A125-25%DR-WORT-ELB-UNI-P1 LEGION #4312-232-8T-ACP-PT-SACH-LBF-RLA NATIONAL #PSPKLA-432-8'-UNV-RSB-.88BF CORONET #BCF-8-232T8-UNV-100%DR-PS RENOVA #MPW8-M-N-432-UNV-14N-NYC-TL LUMAX #WB43296-CO9IA-EAR-PSPH-MNL2-2G-SCA1 | 4 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 PROGRAM RAPID STAR | PENDANT | CORRIDORS, TOILETS, UTILITY/STORAGE ROOMS |  | E2 | 1'X8' PENDANT MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' PENDANT MOUNTED FIXTURE SUITABLE FOR INSTALLATION IN CONTINUOUS ROWS. LENS TO BE 25% DR ACRYLIC. PROVIDE FACTORY INSTALLED "QUICK CONNECTS" | KENALL #R596-132-IS-1-DV LSI #88-8-232-SSO10-UE-DR-SCA MERCURY #M110-132OCT/8T-A125-25%DR-WORT-ELB-UNI-P1 LEGION #4312-132-8T-ACP-PT-SACH-LBF-RLA NATIONAL #PSPKLA-232-8'-UNV-RSB-.88BF CORONET #BCF-8-132T8-UNV-100%DR-PS RENOVA #MPW8-M-N-232-UNV-14N-NYC-TL LUMAX #WB23296-EO9IA-EAR-PSPH-MNL2-2G-SCA1 | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 PROGRAM RAPID STAR | PENDANT | CORRIDORS, TOILETS, UTILITY/STORAGE ROOMS |  | E3 | 1'X8' PENDANT MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
F | 4' LONG OPEN REFLECTOR INDUSTRIAL FIXTURE | LSI #F20-232-SSO10 MERCURY #MIT5-232OCT-ELB-UNI LEGION #2600-232-LBF-RLA NATIONAL #IND-232-T8-VOLT-EB-4' CORONET #H-4-232T8-UNV REVONA #ECS-SGI4-W-N-232-UNV-12N LUMAX #TR23248-EO9-BA | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE/ PENDANT | MECHANICAL/ ELECTRICAL / UTILITY AREA |  | F | 4' LONG OPEN REFLECTOR INDUSTRIAL FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 8' LONG OPEN REFLECTOR INDUSTRIAL FIXTURE | LSI #F20-259-SSO10 MERCURY #MIT5-232OCT/8T-ELB-UNI LEGION #2600-232-8T-LBF-RLA NATIONAL #IND-432-T8-VOLT-EB-8' CORONET #H-8-232T8-UNV REVONA #ECS-SGI8-W-N-432-UNV-12N LUMAX #TR43296-EO9-BA | 4 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE/ PENDANT | MECHANICAL/ ELECTRICAL / UTILITY AREA |  | F1 | 8' LONG OPEN REFLECTOR INDUSTRIAL FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' SURFACE MOUNTED FIXTURE WITH 2-T8 LAMPS, PRISMATIC POLYCARBONATE HIGH IMPACT LENS | KENALL #MLHA12-48-R-MW-CP-232-IS-1-DV LSI #471-S-232-SSO10-.125-UE MERCURY #M30-232OCT-A125/156LEX-ELB-UNI LEGION #641-232-RFL-LBF-RLA NATIONAL #BFPLEX-14-232-T8-SM-VOLT-EB-4' CORONET #BPR-14-232T8-UNV-PC RENOVA #ECS-SMC1-WN-232-UNV-12N-A12PC-TP LUMAX #SU23214-EO9-PCRS | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | PLAYROOMS |  | G | 1'X4' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:2X4 TYPE FIXTURE | 2'X4' SURFACE MOUNTED FIXTURE WITH 2-T8 LAMPS, PRISMATIC POLYCARBONATE HIGH IMPACT LENS | LSI #472-S-432-SSO10-.125-UE MERCURY #M32-432OCT-A125/156LEX-ELB-UNI LEGION #642-432-RFL-LBF-RLA NATIONAL #BFPLEX-24-432-T8-SM-VOLT-EB CORONET #BPR-24-432T8-UNV-PC RENOVA #ECS-SMC4-WN-232-UNV-12N-A12PC-TP LUMAX #SU23224-EO9-PCRS | 4 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | PLAYROOMS |  | G1 | 2'X4' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' PENDANT MOUNTED FIXTURE WITH 2-T8 LAMPS, PRISMATIC POLYCARBONATE HIGH IMPACT LENS | KENALL MLHA12-48-R-MW-CP-232-IS-1-DV LSI #471-S-232-SSO10-.125-UE MERCURY #M32-432OCT-A125/156LEX-ELB-UNI LEGION #641-232-RFL-LBF-RLA NATIONAL #BFPLEX-14-232-T8-PM-VOLT-EB-4' CORONET #BPR-14-232T8-UNV-PC-PS RENOVA #ECS-SMC1-WN-232-UNV-12N-A12PC-TP LUMAX #SU23214-EO9-PCRS-2S | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | PENDANT | PLAYROOMS |  | H | 1'X4' PENDANT MOUNTED FIXTURE | 0.88 | 2 | 25 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' PENDANT MOUNTED FIXTURE WITH 2-T8 LAMPS, PRISMATIC POLYCARBONATE HIGH IMPACT LENS | KENALL #MLHA12-96-R-MW-CP-232-IS-1-DV LSI #471-S-232/2-SSO10-.125-UE MERCURY #M32 432OCT A125/156LEX ELB UNI LEGION #641-232-8T-RFL-LBF-RLA NATIONAL #BFPLEX-18-432-T8-PM-VOLT-EB-8' CORONET #BPR-18-232T8-UNV-PC-PS RENOVA #ECS-SMC18-WN-432-UNV-14N-A12PC-TP LUMAX #SU43218-EO9-FARS | 4 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | PENDANT | PLAYROOMS |  | H1 | 1'X8' PENDANT MOUNTED FIXTURE | 0.88 | 2 | 25 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:2x2 fixture | 2'X2' SURFACE MOUNTED FIXTURE WITH 4-T8 LAMPS, ACRYLIC LENS | LSI #2S-PAX-417-SD-SSO10-UE MERCURY #M34-417OCT-9A125-ELB-UNI-X2 LEGION #42-432-RFA-LBF-RLA NATIONAL #BFPA-22-417-T8-SM-VOLT-EB CORONET #BPR-22-417T8-UNV-PA RENOVA #ECS-SMC2-W-N-417-UNV-14N-PRS LUMAX #41722-CO9-FARS | 4 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | CAFETERIAS |  | I | 2'X2' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 17 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:2X4 TYPE FIXTURE | 2'X4' SURFACE MOUNTED FIXTURE WITH 4-T8 LAMPS, ACRYLIC LENS | LSI #2S-PAX-432-SD-SSO10-UE MERCURY #M32-432OCT-9A125-ELB-UNI LEGION #42-432-RFA-LBF-RLA NATIONAL #BFPA-24-432-T8-SM-VOLT-EB CORONET #BPR-24-432T8-UNV-PA RENOVA #ECS-SMC4-W-N-432-UNV-14N-PRS LUMAX #SU43248-CO9-FARS | 4 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | CAFETERIAS |  | J | 2'X4' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:K TYPE 4X4 FIXTURE | 4'X4' SURFACE MOUNTED FIXTURE WITH 4-T8 LAMPS, ACRYLIC LENS | LSI #2/2S-PAX-232-SD-SSO10-UE MERCURY #M34-432OCT-9A125-ELB-UNI LEGION #44-432-RFA-LBF-RLA NATIONAL #BFPA-44-432-T8-SM-VOLT-EB CORONET #P3644-4T8-PRA-TMW-DW-SC-UNV-SUR RENOVA #ECS-SMC44-W-N-432-UNV-14N-PRS LUMAX #SU43244-CO9-FBRS | 4 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | CORRIDORS |  | K | 4'X4' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:K TYPE 4X4 FIXTURE | 4'X4' SURFACE MOUNTED FIXTURE WITH 6-T8 LAMPS, ACRYLIC LENS | LSI #2/2S-PAX-332-SD-SSO10-UE MERCURY #M34-632OCT-9A125-ELB-UNI LEGION #44-632-RFA-LBF-RLA NATIONAL #BFPA-44-632-T8-SM-VOLT-EB CORONET #P3644-6T8-PRA-TMW-DW-SC-UNV-SUR RENOVA #ECS-SMC44-W-N-632-UNV-23N-PRS LUMAX #SU63244-EO9-FBRS | 6 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | CORRIDORS |  | K1 | 4'X4' SURFACE MOUNTED FIXTURE | 0.88 | 6 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:K TYPE 4X4 FIXTURE | 4'X4' RECESSED MOUNTED FIXTURE WITH 6-T8 LAMPS, ACRYLIC LENS CONFIRM CEILING TYPE | LSI #2/2LA332-SD-SSO10-UE MERCURY #12C-632OCT-9A125-ELB-UNI LEGION #J74-632-RFA-LBF-RLA NATIONAL #RFPA-44-632-T8-XX-VOLT-EB CORONET #P8644-4T8-PRA-DW-SC-UNV RENOVA #ECS-RGT44-W-N-632-UNV-23N-PRS LUMAX #RXX-63244-EO9-FBRS | 6 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | RECESSED | CORRIDORS |  | K2 | 4'X4' RECESSED MOUNTED FIXTURE | 0.88 | 6 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:2x2 fixture | 2'X2' RECESSED MOUNTED FIXTURE WITH 4-T8 LAMPS, ACRYLIC LENS. CONFIRM CEILING TYPE | LSI #LA-417-SD-SSO10-UE MERCURY #12C-417OCT-9A125-ELBS-UNI LEGION #J72-417-RFA-LBF-RLA NATIONAL #RFPA-22-417-T8-XX-VOLT-EB CORONET #REPR-22-417T8-UNV RENOVA #ECS-RGT2-W-N-417-UNV-14N-RST-PRS LUMAX #RXX-41722-CO9-FBRS | 4 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | RECESSED | CAFETERIAS, LOBBIES, CORRIDORS, CLASSROOMS |  | L | 2'X2' RECESSED MOUNTED FIXTURE | 0.88 | 4 | 17 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:2x2 fixture | 2'X2' PENDANT MOUNTED FIXTURE WITH 4-T8 LAMPS, ACRYLIC LENS. CONFIRM CEILING TYPE | LSI #2S-PAX-417-SD-SSO10-UE MERCURY #M34-417OCT-9A125-ELBS-UNI LEGION #42-417-RFA-LBF-RLA NATIONAL #BFPA-22-417-T8-PM-VOLT-EB CORONET #BPR-22-417T8-UNV-PA-PS RENOVA #ECS-SMC2-W-N-417-UNV-14N-RST-PRS LUMAX #SU41722-CO9-FARS-2S | 4 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | PENDANT | CAFETERIAS, LOBBIES, CORRIDORS, CLASSROOMS |  | L1 | 2'X2' PENDANT MOUNTED FIXTURE | 0.88 | 4 | 17 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
| 1'X4' RECESSED MOUNTED FIXTURE WITH 2-T8 LAMPS, ACRYLIC LENS. CONFIRM CEILING TYPE. | LSI #1TGA232-SD-SSO10-UE MERCURY #10C-232OCT-9A125-ELB-UNI LEGION #J71-232-RFA-LBF-RLA NATIONAL #RFPA-14-232-T8-XX-VOLT-EB CORONET #REPR-14-232T8-UNV RENOVA #ECS-RGT1-W-N-232-UNV-12N-PRS LUMAX #RXX-23214-EO9-FARS | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | RECESSED | CAFETERIAS, CORRIDORS |  | M1 | 1'X4' RECESSED MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' RECESSED MOUNTED FIXTURE WITH 4-T8 LAMPS, ACRYLIC LENS. CONFIRM CEILING TYPE. | LSI #1TGA232/2-SD-SSO10-UE MERCURY #10C-232OCT/8T-9A125-CR-ELB-UNI LEGION #J71-232-8T-RFA-LBF-RLA NATIONAL #RFPA-14-232-T8-XX-VOLT-EB CORONET #REPR-18-232T8-UNV RENOVA #2/ECS-RGT-1-W-N-232-UNV-14N-PRS LUMAX #RXX-43218-CO9-FARS | 4 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | RECESSED | CAFETERIAS, CORRIDORS |  | M2 | 1'X8' RECESSED MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' SURFACE MOUNTED FIXTURE WITH 2-T8 LAMPS, ACRYLIC LENS. | LSI #1S-PAX-232-SD-SSO10-UE MERCURY #M30-232OCT-9A125-ELB-UNI LEGION #41-232-RFA-LBF-RLA NATIONAL #BFPA-14-232-T8-SM-VOLT-EB-4' CORONET #BPR-14-232T8-UNV-PA RENOVA #ECS-SMC-1-W-N-232-UNV-12N-PRS LUMAX #SU23214-EO9-FARS | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | CAFETERIAS, CORRIDORS |  | M3 | 1'X4' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' SURFACE MOUNTED FIXTURE WITH 4-T8 LAMPS, ACRYLIC LENS. | LSI #1S-PAX-232/2-SD-SSO10-UE MERCURY #M30-232OCT-9A125-ELBUNI-X2 LEGION #41-232-8T-RFA-LBF-RLA NATIONAL #BFPA-18-432-T8-SM-VOLT-EB CORONET #BPR-18-232T8-UNV RENOVA #ECS-SMC-18-W-N-432-UNV-14N-PRS LUMAX #SU43218-CO9-FARS | 4 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | CAFETERIAS, CORRIDORS |  | M4 | 1'X8' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' PENDENT MOUNTED FIXTURE WITH 2-T8 LAMPS, ACRYLIC LENS. | LSI #1S-PAX-232-SD-SSO10-UE MERCURY #M30-232OCT-9A125-ELB-UNI LEGION #41-232-RFA-LBF-RLA NATIONAL #BFPA-14-232-T8-PM-VOLT-EB-4' CORONET #BPR-14-232T8-UNV-PS RENOVA #ECS-SMC-1-W-N-232-UNV-12N-PRS LUMAX #SU23214-EO9-FARS | 2 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | PENDANT | CAFETERIAS, CORRIDORS |  | M5 | 1'X4' PENDENT MOUNTED FIXTURE | 0.88 | 2 | 25 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' PENDENT MOUNTED FIXTURE WITH 4-T8 LAMPS, ACRYLIC LENS. | LSI #1S-PAX-232/2-SD-SSO10-UE MERCURY #M30-232OCT-9A125-ELB-UNI-X2 LEGION #41-232-8T-RFA-LBF-RLA NATIONAL #BFPA-18-432-T8-PM-VOLT-EB-8' CORONET #BPR-18-232T8-UNV-PS RENOVA #ECS-SMC18-W-N-432-UNV-14N-PRS LUMAX #SU43218-CO9-FARS | 4 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | PENDANT | CAFETERIAS, CORRIDORS |  | M6 | 1'X8' PENDENT MOUNTED FIXTURE | 0.88 | 4 | 25 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:1X3 TYPE FIXTURE | 1'X3' RECESSED MOUNTED FIXTURE WITH 2-T8 LAMPS, 25 WATTS ACRYLIC LENS. CONFIRM CEILING TYPE | LSI #1TXA225-SD-SSO10-UE MERCURY #10C-225OCT-9A125-ELB-UNI-MOD. LEGION #J71-225-RFA-LBF-RLA NATIONAL #RFPA-13-225-T8-XX-VOLT-EB CORONET #REPR-13-225T8-UNV RENOVA #ECS-RGT3-WN-225-UNV-12N-PRS LUMAX #RXX-22513-EO9-FARS | 2 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | RECESSED | CAFETERIAS, CORRIDORS |  | M7 | 1'X3' RECESSED MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:2X4 TYPE FIXTURE | 2'X4' RECESSED MOUNTED FIXTURE WITH 4-T8 LAMPS, ACRYLIC LENS. CONFIRM CEILING TYPE. | LSI #LA432-SD-SSO10-UE MERCURY #11C-432OCT-ELBS-UNI LEGION #J72-432-RFA-LBF-RLA NATIONAL #RFPA-24-432-T8-XX-VOLT-EB CORONET #REPR-24-432T8-UNV RENOVA #ECS-RGT-4-W-N-432-UNV-14N-RST-PRS LUMAX #RXX43224-CO9-FBRS | 4 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | RECESSED | CLASSROOMS, OFFICES, LIBRARY |  | N | 2'X4' RECESSED MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:2X4 TYPE FIXTURE | 2'X4' RECESSED MOUNTED FIXTURE WITH 3-T8 LAMPS, ACRYLIC LENS. CONFIRM CEILING TYPE. | LSI #LA332-SD-SSO10-UE MERCURY #11C-332OCT-ELBS-UNI LEGION #J72-332-RFA-LBF-RLA NATIONAL #RFPA-24-332-T8-XX-VOLT-EB CORONET #REPR-24-332T8-UNV RENOVA #ECS-RGT-4-W-N-332-UNV-13N-RST-PRS LUMAX #RXX-33224-CO9-FBRS-PSP | 3 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | RECESSED | CLASSROOMS, OFFICES, LIBRARY |  | N1 | 2'X4' RECESSED MOUNTED FIXTURE | 0.88 | 3 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:OIL TANK ROOM FIXTURE | PENDANT, SURFACE OR WALL MOUNTED VAPORTIGHT FIXTURE WITH THREADED GUARD, CONFIRM MOUNTING TYPE BEFORE ORDERING | COOPER LIGHTING #PLVS-W/C-GG-42 LITHONIA LIGHTING #VC42LM6 HUBBELL #NV2FG42XHG PHILIPS GUTH # VPW-42T-S BASELITE #W-2-CL-WG-49-42W | 1 | F42- COMPACT FLUORESCENT 4K COLOR TEMP | 120 | INSTANT START | PENDANT, SURFACE, WALL | OIL TANK ROOM |  | O | PENDANT, SURFACE OR WALL MOUNTED VAPORTIGHT FIXTURE | 0.88 | 1 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' SURFACE MOUNTED DECORATIVE LED FIXTURE WITH SINGLE PIECE LENS | KENALL #ME14-S-LED-(XXL40K)-DCC-1-DV PINNACLE #LU14A-35XX-S-UNI-1C-W COLUMBIA #LEPC-14-35-XX-SM-ED-U-NYC MERCURY #LFR-14SM-XX35-UNI-ZKV CREE #CR14-XXL-35K-S/SMK-14-SURFACE |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS | 120 | LED DRIVER INTEGRAL | SURFACE | AUDITORIUM/ CAFETERIA |  | Q | 1'X4' SURFACE MOUNTED DECORATIVE LED FIXTURE | 1 |  |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Block:1X8 Pendant mount | 1'X8' SURFACE MOUNTED DECORATIVE LED FIXTURE WITH SINGLE PIECE LENS | KENALL #ME18-S-LED(XXL40K)-DCC-1-DV PINNACLE #2LU14A-35XX-S-UNI-1C-W COLUMBIA #2LEPC-14-35-XX-SM-ED-U-NYC MERCURY #2LFR-14SM-XX35-UNI-ZKV CREE #CR14-2X-XXL-35K-S/2X-SMK-14-SURFACE-8FT |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS | 120 | LED DRIVER INTEGRAL | SURFACE | AUDITORIUM/ CAFETERIA |  | Q1 | 1'X8' SURFACE MOUNTED DECORATIVE LED FIXTURE | 1 |  |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Block:2X4 TYPE FIXTURE | 2'X4' SURFACE MOUNTED DECORATIVE LED FIXTURE WITH SINGLE PIECE LENS | KENALL #ME24-S-LED-(XXL40K)-DCC-1-DV PINNACLE #LU24A-35XX-S-UNI-1C-W COLUMBIA #LEPC-24-35-XX-SM-ED-U-NYC MERCURY #LFR-24SM-XX35-UNI-ZKV CREE #CR24-XXL-35K-S/SMK-14-SURFACE |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS | 120 | LED DRIVER INTEGRAL | SURFACE | AUDITORIUM/ CAFETERIA |  | Q2 | 2'X4' SURFACE MOUNTED DECORATIVE LED FIXTURE | 1 |  |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Block:1X8 Pendant mount | 1'X8' PENDANT MOUNTED DECORATIVE LED FIXTURE WITH AND SINGLE PIECE LENS | KENALL #ME18-S-LED-(XXL40K)-DCC-1-DV PINNACLE #2LU14A-35XX-P-UNI-1C-W COLUMBIA #2LEPC-14-35-XX-PM-ED-U-NYC MERCURY #2LFR-14PM-XX35-UNI-ZKV CREE #CR14-2X-XXL-35K-S/2X-SMK-14-PENDANT-8FT |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS | 120 | LED DRIVER INTEGRAL | PENDANT | AUDITORIUM/ CAFETERIA |  | Q3 | 1'X8' PENDANT MOUNTED DECORATIVE LED FIXTURE | 1 |  |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Block:1X8 Pendant mount | 1'X8' RECESSED MOUNTED DECORATIVE LED FIXTURE WITH SINGLE PIECE LENS | KENALL #ME18-F-LED(XXL40K)-DCC-1-DV PINNACLE #2LU14A-35XX-UNI-1C-W COLUMBIA #2LEPC-14-35-XX-G-ED-U-NYC MERCURY #2LFR-14G-XX35-UNI-ZKV CREE #CR14-XXL-35K-S-RECESSED-8FT |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS | 120 | LED DRIVER INTEGRAL | RECESSED | AUDITORIUM/ CAFETERIA |  | Q4 | 1'X8' RECESSED MOUNTED DECORATIVE LED FIXTURE | 1 |  |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Block:CLASSROOM FIXTURE | 1'X4' RECESSED MOUNTED DECORATIVE LED FIXTURE WITH SINGLE PIECE LENS | KENALL #ME14-F-LED(XXLXXK)-DCC-1-DV PINNACLE #LU14A-35XX-UNI-1C-W COLUMBIA #LEPC-14-35-XX-G-ED-U-NYC MERCURY #LFR-14G-XX35-UNI-ZKV CREE #CR14-XXL-35K-S-RECESSED-4FT |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS | 120 | LED DRIVER INTEGRAL | RECESSED | AUDITORIUM/ CAFETERIA |  | Q5 | 1'X4' RECESSED MOUNTED DECORATIVE LED FIXTURE | 1 |  |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Block:CFL | 8" RECESSED DOWNLIGHT, LED, WITH DECORATIVE WHITE TRIM RING | IMAGE LIGHTING #MAL8-XX-3-CC-WH PATHWAY LTG #8VLDP-XX-35K/8VLDP-SCL PRESCOLITE #MD8LED-XL-XX-35K/8MD-XL-XFL55-WT PMC #8LE-MX-XX-R-35N-1-L-H VANTAGE # A8VPLED-1-50-35K-L8060-SGC-R | 1 | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS | 120 | LED DRIVER INTEGRAL | RECESSED | AUDITORIUM/ CAFETERIA |  | T | 8" RECESSED DOWNLIGHT, LED, WIT | 1 | 1 |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Block:RECESSED LED | 6" RECESSED LED DOWNLIGHT WITH DECORATIVE SQUARE TRIM | IMAGE LIGHTING #MAL6-XX-3-CC-WH PATHWAY #1XRM-6VLB-XX-35K(*)/1X6VLBSCLPF-1HRM6L14X14 FC LIGHTING #POD 4.1-3K-FL | 1 | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS | 120 | LED DRIVER INTEGRAL | RECESSED | AUDITORIUM/ CAFETERIA |  | T1 | 6" RECESSED LED DOWNLIGHT WITH DECORATIVE SQUARE TRIM | 1 | 1 |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Block:DOUBLE LED | 6" RECESSED LED DOWNLIGHT WITH DECORATIVE SQUARE TRIM - DOUBLE PLATE WITH TWO FIXTURES | PATHWAY #2XRM-6VLB-XX-35K(*)/2X6VLBSCLPF-2HRM6L14X28 FC LIGHTING #POD 4.2-3K-FL VANTAGE #SQ66LEDOP-1-50-35K-LSQ6600-SCL/DOUBLE APERTURE | 2 | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS | 120 | LED DRIVER INTEGRAL | RECESSED | AUDITORIUM/ CAFETERIA |  | T2 | 6" RECESSED LED DOWNLIGHT WITH DECORATIVE SQUARE TRIM - DOUBLE PLATE WITH TWO FIXTURES | 1 | 2 |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Block:TRIPLE LED | PENDANT MOUNTED TRIPLE LED WITH 12" REFRACTORS AND CONICAL LENS | PATHWAY#3P54GAAA-P50/-XX-35/D6-PSTEM-A-1-PA12M VANTAGE #VC1018LED-60-35K-WHT-SCL-TRIPLE CLUSTER | 3 | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS | 120 | LED DRIVER INTEGRAL | PENDANT | AUDITORIUM/ CAFETERIA |  | T3 | PENDANT MOUNTED TRIPLE LED WITH | 1 | 3 |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Block:RECESSED LED | PENDANT MOUNTED SINGLE LED WITH 12" REFRACTORS AND CONICAL LENS | KENALL #EPLB-12-E/O-PM-GW-70L-35K PATHWAY P50/-7-35/D6-PSTEM-A-1-PA12M VANTAGE #VC1018LED-60-35K-WHT-SCL | 1 | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS | 120 | LED DRIVER INTEGRAL | PENDANT | AUDITORIUM/ CAFETERIA |  | T4 | PENDANT MOUNTED SINGLE LED WITH | 1 | 1 |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Block:RECESSED LED | 17" ROUND LED FIXTURE SURFACE MOUNTED | KENALL #MR17FL-MW-50L40K-DV LUMINAIRE #AVR17HO-49WHP-3500K-120-OP-WHT QUALITY #QLP-XXG2-48G2-S-UNV-EZ-WG-TSA APOGEE #S43SCH-2-1-2-1-X-1-4-A | 1 | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS | 120 | LED DRIVER INTEGRAL | SURFACE | AUDITORIUM/ CAFETERIA |  | T5 | 17" ROUND LED FIXTURE | 1 |  |  | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Block:.5 X2 Surface mount | 1/2'X2' SURFACE MOUNTED FIXTURE WITH 2-T8 LAMPS, PRISMATIC POLYCARBONATE HIGH IMPACT LENS | KENALL #MLHA5-24-R-MW-217-IS-1-DV MERCURY #MP65VP-217OCT-ELB-120 LEGION #19-217-UBP-LBF-RLA NATIONAL #CORPU-VP-217-T8-SM-VOLT-EB-2' WILLIAMS #SLF-2-2-17-HIA/TP-EB1-UNV LSI #W44-2-2-17-SSOR-LX-UE CORONET #VP-2-217T8-BP-UNV LUMAX #VL21702-EO9-P-XX | 2 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | STAIRWAYS |  | S1 | 1/2'X2' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 17 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:.5x4 Surface mount | 1/2'X4' SURFACE MOUNTED FIXTURE WITH 2-T8 LAMPS, PRISMATIC POLYCARBONATE HIGH IMPACT LENS | KENALL #MLHA5-48-R-MW-232-IS-1-DV MERCURY #MP65VP-232OCT-ELB-120 LEGION #19-232-UBP-LBF-RLA NATIONAL #CORPU-VP-232-T8-SM-VOLT-EB-4' WILLIAMS #SLF-4-2-32-HIA/TP-EB1-UNV LSI #W44-4-2-32-SSOR-LX-UE CORONET #VP-4-232T8-BP-UNV LUMAX #VL23248-EO9-P-XX | 2 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | STAIRWAYS |  | S2 | 1/2'X4' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:.5x4 Surface mount | 1/2'X4' SURFACE MOUNTED FIXTURE WITH 1-T8 LAMPS, PRISMATIC POLYCARBONATE HIGH IMPACT LENS | KENALL #MLHA5-48-R-MW-132-IS-1-DV MERCURY #MP65VP-132OCT-ELB-120 LEGION #19-132-UBP-LBF-RLA NATIONAL #CORPU-VP-132-T8-SM-VOLT-EB-4' WILLIAMS #SLF-4-1-32-HIA/TP-EB1-UNV LSI #W44-4-1-32-SSOR-LX-UE CORONET #VP-4-132T8-BP-UNV LUMAX #VL13248-EO9-P-XX | 1 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | STAIRWAYS |  | S3 | 1/2'X4' SURFACE MOUNTED FIXTURE | 0.88 | 1 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:.5 X2 Surface mount | 1/2'X2' SURFACE MOUNTED FIXTURE WITH 1-T8 LAMPS, PRISMATIC POLYCARBONATE HIGH IMPACT LENS | KENALL #MLHA5-48-R-MW-117-IS-1-DV MERCURY #MP65VP-117OCT-ELB-120 LEGION #19-117-UBP-LBF-RLA NATIONAL #CORPU-VP-117-T8-SM-VOLT-EB-2' WILLIAMS #SLF-2-1-17-HIA/TP-EB1-UNV LSI #W44-2-1-17-SSOR-LX-UE CORONET #VP-2-117T8-BP-UNV LUMAX #VL11702-EO9-P-XX | 1 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | STAIRWAYS |  | S4 | 1/2'X2' SURFACE MOUNTED FIXTURE | 0.88 | 1 | 17 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:.5x4 Surface mount | 1/2'X4' PENDANT MOUNTED FIXTURE WITH 1-T8 LAMPS, PRISMATIC POLYCARBONATE HIGH IMPACT LENS | KENALL #MLHA5-48-R-MW-132-IS-1-DV MERCURY #MP65VP-132OCT-ELB-120 LEGION #19-232-UBP-LBF-RLA NATIONAL #CORPU-VP-132-T8-pM-VOLT-EB-4' WILLIAMS #SLF-4-1-32-HIA/TP-EB1-UNV-PENDANT LSI #W44-4-1-32-SSOR-LX-UE-PENDANT CORONET #VP-4-132T8-BP-UNV-PS LUMAX #VL13248-EO9-P-XX | 1 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | PENDANT | STAIRWAYS |  | S5 | 1/2'X4' PENDANT MOUNTED FIXTURE | 0.88 | 1 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:.5 X2 Surface mount | 1/2'X2' SURFACE MOUNTED FIXTURE WITH 2-T8 LAMPS AND SIDE BUILT IN GFI SWITCH AND OUTLET | KENALL #R524-217T8-IS-1-120-RS-GFI MERCURY #MP15-217OCT-A-ELB-RKS-GFI-ELB120 LEGION LIGHTING #19-217-UBP-LBF-RLA NATIONAL #CORPU-VP-217-T8-SM-VOLT-EB-RKS-GFI-4' WILLIAMS SLF-2-2-17-HIA/TP-EB1-UNV-GFI LSI W44-2-2-17-SSOHLR-UE-GFI | 2 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | STAIRWAYS |  | S11 | 1/2'X2' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 17 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:CFL | 13" ROUND COMPACT FLUORESCENT FIXTURE SURFACE MOUNTED (WALL OR CEILING) VANDAL RESISTANT | KENALL #MR13FL-MW-42P-1-DV LSI # EURM-OB-42-CFL-W-UE-WHT PMC #RD-MD-1/42TT-WHITELENS-BZHOUSING-DT | 1 | F42PLT- COMPACT FLUORESCENT 4K COLOR TEMP | 120 | RAPID START | SURFACE | MECHANICAL/ ELECTRICAL/ UTILITY AREA/ CROWL SPACE/ STORAGE/ TOILETS |  | U | 13" ROUND COMPACT FLUORESCENT FIXTURE | 1 | 1 | 42 | F42PLT- COMPACT FLUORESCENT 4K COLOR TEMP
Block:14 inch ROUND FIXTURE | 12" ROUND COMPACT FLUORESCENT FIXTURE PENDANT MOUNTED DROP CORD OR STEM MOUNT (CONFIRM MOUNTING TYPE PRIOR TO ORDERING) | DURAGUARD #D-42W-CFL-VP43-VS30S HUBBELL #NV2FG42XSG-NVPSD12 EXCELINE #RDB42HFLCGC8 | 1 | F42PLT- COMPACT FLUORESCENT 4K COLOR TEMP | 120 | RAPID START | PENDANT | MECHANICAL/ ELECTRICAL/ UTILITY AREA/ CROWL SPACE/ STORAGE/ TOILETS |  | U1 | 12" ROUND COMPACT FLUORESCENT FIXTURE | 1 | 1 | 42 | F42PLT- COMPACT FLUORESCENT 4K COLOR TEMP
Block:14 inch Square fixture | 14" SQUARE SURFACE MOUNTED COMPACT FLUORESCENT FIXTURE (WALL OR CEILING) VANDAL RESISTANT | PINNACLE #CJ11A-1CF32RS-S-UNV-1C-W KENALL #S1414D-C-MW-32P-2 FC LIGHTING # FCW3360-120V-PL-2/32Q-BK | 2 | F32PLT COMPACT FLUORESCENT 4K COLOR TEMP | 120 | RAPID START | SURFACE | OFFICES/ LOBBY/ CORRIDOR/ AUDITORIUM/ |  | U2 | 14" SQUARE SURFACE MOUNTED COMPACT FLUORESCENT FIXTURE | 1 | 2 | 32 | F32PLT COMPACT FLUORESCENT 4K COLOR TEMP
Block:14 inch Square fixture | 1'X1' SQUARE RECESSED MOUNTED COMPACT FLUORESCENT FIXTURE CONFIRM CEILING TYPE PRIOR TO ORDERING | KENALL #ME11MRI-24L40-24VDC-CAP LEGION #5711-12D38 PINNACLE #CJ11A-1CF32RS-UNV-IC-W LUMAX #3PF13211-TE9-LO4 WILLIAMS #HET-1-142-A-EB1-UNV | 1 | F42 COMPACT FLUORESCENT 4K COLOR TEMP OR 24W LED | 120 | RAPID START | RECESSED | OFFICES/ LOBBY/ CORRIDOR/ AUDITORIUM/ |  | U3 | 1'X1' SQUARE RECESSED MOUNTED COMPACT FLUORESCENT FIXTURE | 1 | 1 | 42 | F42 COMPACT FLUORESCENT 4K COLOR TEMP OR 24W LED
Block:14 inch ROUND FIXTURE | 12" ROUND COMPACT FLUORESCENT FIXTURE PENDANT MOUNTED VANDAL RESISTANT DROP CORD OR STEM MOUNT | KENALL #EPLB-12-E/O-PM-GW-1-32P PATHWAY #P71-142-E4-P-XX-A FC LIGHTING #FCP660-120V-PL-32T-SA-RA-DBC LUMINIS # PR1240-F132-120V-WHT | 1 | F42 COMPACT FLUORESCENT 4K COLOR TEMP OR 24W LED | 120 | RAPID START | PENDANT | OFFICES/ LOBBY/ CORRIDOR/ AUDITORIUM/ |  | U4 | 12" ROUND COMPACT FLUORESCENT FIXTURE | 1 | 1 | 42 | F42 COMPACT FLUORESCENT 4K COLOR TEMP OR 24W LED
Block:.5x4 Surface mount | COVE LIGHT WITH 1-T8 LAMPS- PROVIDE CLEAR DUST COVER | METALUMEN #FSE-B-4-C-W-T8-DV MERCURY #ST232OCT-ELB-UNI-TG LEGION #2615-232-LBF-RLA NATIONAL #CV83-232-T8-VOLT-EB-DUST COVER DAY-O-LITE ITG-38-I-232T8-EX-4-W CORONET #S-232T8UNV-ASYM-DCBYOTHERS | 1 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | INSTANT START | COVE | LOBBIES, AUDITORIUM |  | V | COVE LIGHT WITH 1-T8 LAMPS- | ? | 1 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:.5x4 Surface mount | DISPLAY LIGHT 1'X4' WITH 1-T8 LAMPS | KENALL #FNL6-48-MW-CP-132-35K-IS-1-120 LEGION #584-132-MW-EBO LITHONIA #TLWAD-132-WPB-R4-120-GEB10-LP835-C041 | 1 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | INSTANT START | WALL MOUNT | LOBBIES, AUDITORIUM |  | V1 | DISPLAY LIGHT 1'X4' WITH 1-T8 L | ? | 1 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' SURFACE MOUNTED FIXTURE WITH 2-T8 LAMPS, ACRYLIC LENS, GASKETED, SUITABLE FOR WET LOCATIONS, VERMIN-PROOF, NSF2 SPLASH ZONE LISTED, ONE-PIECE INSET DOOR | KENALL #CSESI-14-232-IS-1-DV-2F-2H-1 CETROLUX #CRS-1X4-3555-A/A-232T8-N-120 LC DOANE #RXS1-2/32IS-VAR-CW12-NS-RLA LUMINARIE #VPF-12-4-2F32T8-120-OP-WHT-WET-NSF | 2 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | WALL-MOUNT | KITCHEN |  | W1 | 1'X4' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' RECESSED MOUNTED FIXTURE WITH 2-T8 LAMPS, ACRYLIC LENS, GASKETED, SUITABLE FOR WET LOCATIONS, VERMIN-PROOF, NSF2 SPLASH ZONE LISTED, ONE-PIECE INSET DOOR CONFIRM CEILING TYPE PRIOR TO ORDERING | KENALL #CSEFI-14T8-232-IS-1-DV-2F-2H-1 MERCURY #SAF-14-232OCT-P5-ELB-UNI LC DOANE #RXB1-2/32IS-VAR-CW12-NS-RLA PHILIPS GUTH # K2A14-2F32-AP3 NEWSTAR #SCG14-HC-OC-2-32-1-B-UN-NSF | 2 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | RECESSED | KITCHEN |  | W2 | 1'X4' RECESSED MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:CLASSROOM FIXTURE | 1'X4' PENDANT MOUNTED FIXTURE WITH 2-T8 LAMPS, ACRYLIC LENS, GASKETED, SUITABLE FOR WET LOCATIONS, VERMIN-PROOF, NSF2 SPLASH ZONE LISTED, ONE-PIECE INSET DOOR | KENALL #CSESI-14-232-IS-1-DV-2F-2H-1 CETROLUX #CRP-1X4-3555-A/A-232T8-N-120 LC DOANE #RXS1-2/32IS-VAR-CW12-NS-RLA LUMINAIRE #VPF12-4-2F32T8-120CP-WHT-NSF | 2 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | PENDANT | KITCHEN |  | W3 | 1'X4' PENDANT MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' SURFACE MOUNTED FIXTURE WITH 2-T8 LAMPS, ACRYLIC LENS, GASKETED, SUITABLE FOR WET LOCATIONS, VERMIN-PROOF, NSF2 SPLASH ZONE LISTED, ONE-PIECE INSET DOOR | KENALL #CSESI-18-232-IS-1-DV-2F-2H-1 CETROLUX #CRS-1X8-3555-A/A-232T8-N-120 LC DOANE #RXS1-2/32IS-VAR-CW12-NS-8'-RLA LUMINARIE #VPF-12-4-2F32T8-120-OP-WHT-WET-NSF-PENDANT-JB-8FT | 4 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | KITCHEN |  | W4 | 1'X8' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' RECESSED MOUNTED FIXTURE WITH 2-T8 LAMPS, ACRYLIC LENS, GASKETED, SUITABLE FOR WET LOCATIONS, VERMIN-PROOF, NSF2 SPLASH ZONE LISTED, ONE-PIECE INSET DOOR CONFIRM CEILING TYPE PRIOR TO ORDERING | KENALL #CSEFI-18T8-232-IS-1-DV-2F-2H-1 MERCURY #SAF-14-232OCT-P5-ELB-UNI-X2 LC DOANE #RXB1-2/32IS-VAR-CW12-NS-RLA PHILIPS GUTH # K2A14-2F32-AP3-2-TANDEM NEWSTAR #SCG14-HC-OC-2-32-1-B-UN-TANDEM 8FT | 4 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | RECESSED | KITCHEN |  | W5 | 1'X8' RECESSED MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:1X8 Pendant mount | 1'X8' PENDANT MOUNTED FIXTURE WITH 2-T8 LAMPS, ACRYLIC LENS, GASKETED, SUITABLE FOR WET LOCATIONS, VERMIN-PROOF, NSF2 SPLASH ZONE LISTED, ONE-PIECE INSET DOOR | KENALL #CSESI-18-232-IS-1-DV-2F-2H-1 CETROLUX #CRP-1X8-3555-A/A-232T8-N-120 LC DOANE #RXS1-2/32IS-VAR-CW12-NS-8'-RLA LUMINARIE #VPF-12-4-2F32T8-120-OP-WHT-WET-NSF-PENDANT-JB-8FT | 4 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | PENDANT | KITCHEN |  | W6 | 1'X8' PENDANT MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:1X2 Surface mount | 1'X2' SURFACE MOUNTED FIXTURE WITH 2-T8 LAMPS, ACRYLIC LENS, GASKETED, SUITABLE FOR WET LOCATIONS, VERMIN-PROOF, NSF2 SPLASH ZONE LISTED, IP65 RATED, 18 GUAGE CONSTRUCTION | KENALL #CSESI-12-217-IS-1-DV-2F-2H-1 CETROLUX #CRS-1X4-3555-A/A-217T8-N-120 LC DOANE #RXS1-2/17IS-VAR-CW12-NS-RLA LUMINARIE #VPF-12-2-2F17T8-120-OP-WHT-WET-NSF-PENDANT | 2 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP | 120 | .88 INSTANT START | SURFACE | KITCHEN |  | W7 | 1'X2' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Block:LED recessed | SURFACE MOUNT LED HIGHBAY FIXTURE WITH TEXTURED ACRYLIC LENS | KENALL #TD17/HBMA26-DTS-5N-TP-MW-(108L40)-DV HUBBELL #HBL-60L-U-X2-35K-N-WH-WG LUSIO #LW-LUSIO-ES-BAY-4MS-NW-FR-SUR-120-WG YS LIGHTING #FYGC31-II-120-84-100-4K-SURFACE |  | 8000 LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 7000 LUMENS | 120 | LED DRIVER INTEGRAL | SURFACE | GYMNASIUM |  | Y | SURFACE MOUNT LED HIGHBAY FIXTURE | 1 |  |  | 8000 LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 7000 LUMENS
Block:LED recessed | LED HIGHBAY FIXTURE WITH TEXTURED ACRYLIC LENS AND STEM PENDANT | KENALL #TD17/HBMA26/EPLB-PM-5N-TP-SL-LED(108L40)-DV HUBBELL #HBL-60L-U-S2-35K-N-WH-WG LUSIO #LW-LUSIO-ES-BAY-4MS-NW-FR-STEM-120-WG YS LIGHTING #FYGC31-II-120-84-100-4K-STEM MTD XTRALIGHT # LHPLED-206-100-4A-UNI-X-W |  | 8000 LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 7000 LUMENS | 120 | LED DRIVER INTEGRAL | PENDANT | GYMNASIUM |  | Y1 | LED HIGHBAY FIXTURE | 1 |  |  | 8000 LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 7000 LUMENS
Block:LED recessed | RECESSED MOUNT HIGHBAY LED WITH TEXTURED ACRYLIC LENS AND DECORATIVE CEILING TRIM RING | KENALL #EPLB-16-RECESSED-O-LED(108L40)-DV-WG EVOLUCIA #EVO-DL-2500-4K-52-UNV-R-S-P YS #FYGC31-II-120-84-100-4K-RECESSING KIT |  | 8000 LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 7000 LUMENS | 120 | LED DRIVER INTEGRAL | RECESSED | GYMNASIUM |  | Y2 | RECESSED MOUNT HIGHBAY LED WIT | 1 |  |  | 8000 LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 7000 LUMENS

## Fix Data
FIXT. TYPE | MANUFACTURER'S DESCRIPTION | Ballast Factor | LAMPS | Watts |  | Exit Sign FIXT. TYPE | MANUFACTURER'S DESCRIPTION | Ballast Factor | LAMPS | Watts | Number of Faces
- | - | 0 | 0 | 0 |  | - | - | 0 | 0 | 0
A1 | 1'X8' PENDANT MOUNTED FIXTURE | 1.15 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | X1 | EDGE MOUNT-SINGLE FACE- LED EXIT SIGNAGE | 1 | 1 | 3.5 | 1
A2 | 1'X4' PENDANT MOUNTED FIXTURE | 1.15 | 1 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | X2 | EDGE MOUNT-DOUBLE FACE- LED EXIT SIGNAGE | 1 | 1 | 3.5 | 2
A3 | 1'X8' PENDANT MOUNTED FIXTURE | 1.15 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | X3 | PENDANT MOUNT-SINGLE FACE-LED EXIT SIGNAGE | 1 | 1 | 3.5 | 1
A4 | 1'X4' PENDANT MOUNTED FIXTURE | 1.15 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | X4 | PENDANT MOUNT-DOUBLE FACE-LED EXIT SIGNAGE | 1 | 1 | 3.5 | 2
A5 | 1'X3' PENDANT MOUNTED FIXTURE | 1.15 | 1 | 25 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | X5 | WALL SURFACE MOUNT-SINGLE FACE-LED EXIT SIGNAGE | 1 | 1 | 3.5 | 1
A6 | 1'X4' PENDANT MOUNTED FIXTURE | 1.15 | 3 | 32 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | Cust- X1 | --- | - | - | -
A7 | 1'X8' PENDANT MOUNTED FIXTURE | 0.88 | 2 | 32 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | Cust- X2 | --- | - | - | -
A8 | 1'X4' PENDANT MOUNTED FIXTURE | 0.88 | 1 | 32 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | Cust- X3 | --- | - | - | -
B1 | 1'X8' SURFACE MOUNTED FIXTURE | 1.15 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP | Cust- X4 | --- | - | - | -
B2 | 1'X4' SURFACE MOUNTED FIXTURE | 1.15 | 1 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
B3 | 1'X8' SURFACE MOUNTED FIXTURE | 1.15 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
B4 | 1'X4' SURFACE MOUNTED FIXTURE | 1.15 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
B4 | 1'X3' SURFACE MOUNTED FIXTURE | 1.15 | 1 | 32 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
C | 1'X4' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
C1 | 1'X8' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
CF | REPLACE LAMP WITH COMPACT FLUORESCENT | 1 | 1 | 32 | 32W- COMPACT FLUORESCENT 4K COLOR TEMP
D | 1'X4' SURFACE MOUNTED WRAPAROUND FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
D1 | 1'X4' PENDANT MOUNTED WRAPAROUND FIXTURE | 0.88 | 2 | 32 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
E | 1'X4' PENDANT MOUNTED FIXTURE | 0.88 | 2 | 32 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
E1 | 1'X4' PENDANT MOUNTED FIXTURE | 0.88 | 1 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
E2 | 1'X8' PENDANT MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
E3 | 1'X8' PENDANT MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
F | 4' LONG OPEN REFLECTOR INDUSTRIAL FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
F1 | 8' LONG OPEN REFLECTOR INDUSTRIAL FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
G | 1'X4' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
G1 | 2'X4' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
H | 1'X4' PENDANT MOUNTED FIXTURE | 0.88 | 2 | 32 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
H1 | 1'X8' PENDANT MOUNTED FIXTURE | 0.88 | 2 | 32 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
I | 2'X2' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 17 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
J | 2'X4' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
K | 4'X4' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
K1 | 4'X4' SURFACE MOUNTED FIXTURE | 0.88 | 6 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
K2 | 4'X4' RECESSED MOUNTED FIXTURE | 0.88 | 6 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
L | 2'X2' RECESSED MOUNTED FIXTURE | 0.88 | 1 | 39.3 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
L1 | 2'X2' PENDANT MOUNTED FIXTURE | 0.88 | 4 | 17 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
M1 | 1'X4' RECESSED MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
M2 | 1'X8' RECESSED MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
M3 | 1'X4' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
M4 | 1'X8' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
M5 | 1'X4' PENDENT MOUNTED FIXTURE | 0.88 | 2 | 32 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
M6 | 1'X8' PENDENT MOUNTED FIXTURE | 0.88 | 4 | 32 | F25T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
M7 | 1'X3' RECESSED MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
N | 2'X4' RECESSED MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
N1 | 2'X4' RECESSED MOUNTED FIXTURE | 0.88 | 3 | 32 | F32T8 LOW MERCURY EXTRA LONG LIFE 4100K COLOR TEMP
O | VAPORTIGHT FIXTURE WITH THREADED GUARD-F42- COMPACT FLUORESCENT | 1 | 1 | 42
Q | 1'X4' SURFACE MOUNTED DECORATIVE LED FIXTURE | 1 | 1 | 108 | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Q1 | 2'X2' SURFACE MOUNTED DECORATIVE LED FIXTURE | 1 | 1 | Custom | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Q2 | 2'X4' SURFACE MOUNTED DECORATIVE LED FIXTURE | 1 | 1 | Custom | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Q3 | 1'X8' PENDANT MOUNTED DECORATIVE LED FIXTURE | 1 | 1 | Custom | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Q4 | 1'X8' RECESSED MOUNTED DECORATIVE LED FIXTURE | 1 | 1 | Custom | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
Q5 | 1'X4' RECESSED MOUNTED DECORATIVE LED FIXTURE | 1 | 1 | Custom | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
T | 8" RECESSED DOWNLIGHT, LED, WITH DECORATIVE WHITE TRIM RING | 1 | 1 | 27.6 | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
T1 | 6" RECESSED LED DOWNLIGHT | 1 | 1 | Custom | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
T2 | 6" RECESSED LED DOWNLIGHT - DOUBLE PLATE WITH TWO FIXTURES | 1 | 2 | Custom | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
T3 | PENDANT MOUNTED TRIPLE LED WITH 12" REFRACTORS AND CONICAL LENS | 1 | 3 | Custom | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
T4 | PENDANT MOUNTED SINGLE LED WITH 12" REFRACTORS AND CONICAL LENS | 1 | 1 | 32 | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
T5 | 17" ROUND LED FIXTURE | 1 | 1 | Custom | XX LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 5000 LUMENS
S1 | 1/2'X2' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 17 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
S2 | 1/2'X4' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
S3 | 1/2'X4' SURFACE MOUNTED FIXTURE | 0.88 | 1 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
S4 | 1/2'X2' SURFACE MOUNTED FIXTURE | 0.88 | 1 | 17 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
S5 | 1/2'X4' PENDANT MOUNTED FIXTURE | 0.88 | 1 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
S11 | 1/2'X2' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 17 | F17T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
U | 13" ROUND COMPACT FLUORESCENT FIXTURE | 1 | 1 | 42 | F42PLT- COMPACT FLUORESCENT 4K COLOR TEMP
U1 | 12" ROUND COMPACT FLUORESCENT FIXTURE | 1 | 1 | 42 | F42PLT- COMPACT FLUORESCENT 4K COLOR TEMP
U2 | 14" SQUARE SURFACE MOUNTED COMPACT FLUORESCENT FIXTURE | 1 | 2 | 32 | F32PLT COMPACT FLUORESCENT 4K COLOR TEMP
U3 | 1'X1' SQUARE RECESSED MOUNTED COMPACT FLUORESCENT FIXTURE | 1 | 1 | 42 | F42 COMPACT FLUORESCENT 4K COLOR TEMP OR 24W LED
U4 | 12" ROUND COMPACT FLUORESCENT FIXTURE | 1 | 1 | 42 | F42 COMPACT FLUORESCENT 4K COLOR TEMP OR 24W LED
V | COVE LIGHT WITH 1-T8 LAMPS- | 0.88 | 1 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
V1 | DISPLAY LIGHT 1'X4' WITH 1-T8 L | 0.88 | 1 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
V2 | DISPLAY LIGHT 1'X3' WITH 1-T8 L | 0.88 | 1 | 25
W1 | 1'X4' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
W2 | 1'X4' RECESSED MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
W3 | 1'X4' PENDANT MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
W4 | 1'X8' SURFACE MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
W5 | 1'X8' RECESSED MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
W6 | 1'X8' PENDANT MOUNTED FIXTURE | 0.88 | 4 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
W7 | 1'X2' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32 | F32T8 LOW MERCURY LONG LIFE 4100K COLOR TEMP
Y | SURFACE MOUNT LED HIGHBAY FIXTURE WITH TEXTURED ACRYLIC LENS | 1 | 1 | 55.4 | 8000 LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 7000 LUMENS
Y1 | LED HIGHBAY FIXTURE WITH TEXTURED ACRYLIC LENS AND STEM PENDANT | 1 | 1 | 85 | 8000 LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 7000 LUMENS
Y2 | RECESSED MOUNT HIGHBAY LED WITH TEXTURED ACRYLIC LENS | 1 | 1 | Custom | 8000 LUMENS LED ARRAY >80 CRI 3500 K (*) OPTICS MINIMUM 7000 LUMENS
O1 | 4' HAZARDOUS LOCATION LTG. FIXT, 20 GAUGE CRC HOUSING WITH ACRYLIC LENS COMPLETELY SEALED AND GASKETED. CONFIRM MOUNTING TYPE BEFORE ORDERING | 0.88 | 2 | 32
W9 | 1'X1' RECESSED MOUNTED FIXTURE WITH GASKETED ACRYLIC LENS, SUITABLE FOR WET LOCATIONS, VERMIN-PROOF, NSF2 SPLASH ZONE LISTED, IP65 RATED, 18 GUAGE CONSTRUCTION CONFIRM CEILING TYPE PRIOR TO ORDERING | 0.88 | 3 | 32
B8 | 1'X8' SURFACE MOUNTED FIXTURE | 0.88 | 1 | 32
G2 | 1'X8' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32
M17 | 1'X8' RECESSED MOUNTED FIXTURE | 0.88 | 2 | 32
M18 | 1'X4' RECESSED MOUNTED FIXTURE | 0.88 | 1 | 32
N2 | 2'X4' RECESSED MOUNTED FIXTURE | 0.88 | 2 | 32
M15 | 1'X8' RECESSED MOUNTED FIXTURE | 1.15 | 2 | 32
M16 | 1'X4' RECESSED MOUNTED FIXTURE | 1.15 | 1 | 32
M8 | 1/2'X4' RECESSED MOUNTED FIXTURE | 0.88 | 2 | 32
T12A | 8" RECESSED DOWNLIGHT, LED, WITH DECORATIVE WHITE TRIM RING | 1 | 1 | 27.6
T4A | PENDANT MOUNTED SINGLE LED WITH 12" REFRACTORS AND CONICAL LENS | 1 | 1 | 32
DA | 1'X4' SURFACE MOUNTED WRAPAROUND FIXTURE | 0.88 | 1 | 32
D1A | 1'X4' PENDANT MOUNTED WRAPAROUND FIXTURE | 0.88 | 1 | 32 | 32
B7 | 1'X8' SURFACE MOUNTED FIXTURE | 0.88 | 2 | 32
Cust-16 | --- | - | - | -
Cust-17 | --- | - | - | -
Cust-18 | --- | - | - | -
Cust-19 | --- | - | - | -
Cust-20 | --- | - | - | -
Cust-21 | --- | - | - | -
Cust-22 | --- | - | - | -
Cust-23 | --- | - | - | -
Cust-24 | --- | - | - | -
Cust-25 | --- | - | - | -